## Sheet1
Document: |  | SUB-AP-24-165-INS | Alexion AXD020 WIFI Pre-Heat Project
Date: |  | 2025-01-20
Generated By: |  | Zain Kenny
Revision: |  | 0
Technical Review: |  | Conor Cassin
Quality Review: |  | Aishling Kelly
No. | Instrument Tag | Service | Instrument Description | Instrument Manufacturer | Instrument Model | Process Connection | Material | Auxillary Switches | Order Code | Immersion Length (mm) | Lagging Length (mm) | Fluid | Min Range | Max Range | Unit | Setpoint | Line Size (mm) | Control Signal | Supplied By | COMMENTS
1 | TT-103211-500 | PLC | UF Water Flow Temperature Transmitter-Meco & BMS | Endress & Hauser | TM411 | Tri-Clamp | SS | n/a | TM411-6HDQ0/125 | 50 | 30 | UF | -10 | 100 | °C | TBC | 80 | 4-20 mA Loop Powered | Subnet
2 | TT-103211-501 | nQBMS | UF Water Flow Temperature Transmitter | Endress & Hauser | TM411 | Tri-Clamp | SS | n/a | TM411-6HDQ0/125 | 50 | 30 | UF | -10 | 100 | °C | TBC | 80 | 4-20 mA Loop Powered | Subnet
3 | TT-103211-502 | nQBMS | HHW Flow Temperature Transmitter | Endress & Hauser | TM121 | G1/2” Male Thread | SS | n/a | TM121-VEF6/101 | 60 | 40 | HHW | -10 | 100 | °C | TBC | 100 | 4-20 mA Loop Powered | Subnet
4 | TT-103211-503 | nQBMS | HHW Return Temperature Transmitter | Endress & Hauser | TM121 | G1/2” Male Thread | SS | n/a | TM121-VEF6/101 | 60 | 40 | HHW | -10 | 100 | °C | TBC | 100 | 4-20 mA Loop Powered | Subnet
05 | FIT-124451-001 | nQBMS | Chilled Water Return Flow Transmitter | Endress & Hauser | Proline Promag P300 | PN16 Flange EN-1092-1 |  | n/a | 5P3B80-AAIBAEAFAAED3K0AA2+AAZ1 | n/a | n/a |  | 0 | 3000 | l/min | 1303 l/min | 150 | 4-20mA (Passive) | Subnet
06 | PDT-124451-003 | nQBMS | CHW Generation Pressure Differential Transmitter | Endress & Hauser | Deltabar PMD55B | G1/2 EN837 |  | n/a | PMD55B-AABACJA37HBGSAJA1B+F1JANRQ1Z1 | n/a | n/a |  | 0 | 6 | bar | TBC | 150 | 4-20 mA Loop Powered | Subnet
07 | PDSH-124451-001 | nQBMS | CHW Deaerator Filter Pressure Differential Switch High | Endress & Hauser | Cerabar PMP21 | G1/2 EN837 |  | RMA42 | PMP21-AA1A1NBWBJ+F3JAZ1 (x2) | n/a | n/a |  | 0 | 0.075 | bar | TBC | 150 | 4-20 mA Loop Powered | Subnet
08 | PIT-124451-001 | nQBMS | CHW Supply Pressure Transmitter | Endress & Hauser | Cerabar PMP51B | G1/2 EN837 |  | n/a | PMP51B-AABACBA6AA3PBI1WBJA1+Z1 | n/a | n/a |  | 0 | 10 | Bar | TBC | 150 | 4-20 mA Loop Powered | Subnet
09 | PDT-124451-006 | nQBMS | CHW Supply Pressure Differential Transmitter | Endress & Hauser | Deltabar PMD55B | G1/2 EN837 |  | n/a | PMD55B-AABACJA37HBGSAJA1B+F1JANRQ1Z1 | n/a | n/a |  | 0 | 6 | bar | TBC | 15 | 4-20 mA Loop Powered | Subnet
10 | PSH-124451-001 | nQBMS | CHW Supply Pressure Switch High | Endress & Hauser | Cerabar PMP21 | G1/2 EN837 |  | RMA42 | PMP21-AA1A1NBWBJ+F3JAZ1 | n/a | n/a |  | 0 | 9.8 | bar | TBC | 15 | 4-20 mA Loop Powered | Subnet
11 | PDT-124451-002 | nQBMS | CHW End of Line Pressure Differential Transmitter | Endress & Hauser | Deltabar PMD55B | G1/2 EN837 |  | n/a | PMD55B-AABACJA37HBGSAJA1B+F1JANRQ1Z1 | n/a | n/a |  | 0 | 6 | bar | TBC | 20 | 4-20 mA Loop Powered | Subnet
12 | PDT-124451-004 | nQBMS | CHW End of Line Pressure Differential Transmitter | Endress & Hauser | Deltabar PMD55B | G1/2 EN837 |  | n/a | PMD55B-AABACJA37HBGSAJA1B+F1JANRQ1Z1 | n/a | n/a |  | 0 | 6 | bar | TBC | 32 | 4-20 mA Loop Powered | Subnet
13 | PDT-124451-005 | nQBMS | CHW End of Line Pressure Differential Transmitter | Endress & Hauser | Deltabar PMD55B | G1/2 EN837 |  | n/a | PMD55B-AABACJA37HBGSAJA1B+F1JANRQ1Z1 | n/a | n/a |  | 0 | 6 | bar | TBC | 40 | 4-20 mA Loop Powered | Subnet
14 | PDT-124451-001 | nQBMS | CHW End of Line Pressure Differential Transmitter | Endress & Hauser | Deltabar PMD55B | G1/2 EN837 |  | n/a | PMD55B-AABACJA37HBGSAJA1B+F1JANRQ1Z1 | n/a | n/a |  | 0 | 6 | bar | TBC | 15 | 4-20 mA Loop Powered | Subnet
5 | FIT-103211-500 | nQBMS | HHW Water Flow Meter | Endress & Hauser | Proline Promag W 10 | PN40 Flange EN-1092-1 | PTFE | n/a | 5WBB1H-RVR9/101 | n/a | n/a | HHW | 0 | 20 | l/s | TBC | 100 | 4-20 mA Loop Powered | Subnet
06 | FM-002A | nQBMS | UF Water Flow Meter | Endress & Hauser | Proline Promag P300 | PN40 Flange EN-1092-1 | PTFE | n/a | 5P3B80-264K0/101 | n/a | n/a | UF | 0 | 40 | l/s | TBC | 80 | 4-20 mA Loop Powered | Subnet | EM3 to confirm
07 | CV-001 | nQBMS | 2 Port Control Valve-Meco & BMS | Emerson | Fisher DX | TBC |  | TBC | TBC | TBC | TBC |  | TBC | TBC | TBC | TBC | TBC | TBC | TBC
6 | TT-103212-500 | PLC | UF Water Flow Temperature Transmitter-Meco & BMS | Endress & Hauser | TM411 | Tri-Clamp | SS | n/a | TM411-6HDQ0/125 | 50 | 30 | UF | -10 | 100 | °C | TBC | 80 | 4-20 mA Loop Powered | Subnet
19 | FIT-124951-001 | nQBMS | HW Return Generation Flow Transmitter | Endress & Hauser | TM411 | G1/2” Male Thread |  | n/a | TM411-6HDQ0/101 | n/a | n/a |  | 0 | 3000 | l/min | TBC | 150 | 4-20mA (Passive) | Subnet
20 | PDT-124951-001 | nQBMS | HW Pressure Differential Transmitter | Endress & Hauser | Deltabar PMD55B | G1/2 EN837 |  | n/a | TM121-HJXO/101 | n/a | n/a |  | 0 | 6 | bar | TBC | 15 | 4-20 mA Loop Powered | Subnet
21 | PDSH-124951-001 | nQBMS | HW Deaerator Filter Pressure Differential Switch High | Endress & Hauser | Cerabar PMP21 | G1/2 EN837 |  | RMA42 | TM121-HJXO/101 | n/a | n/a |  | 0 | 0.03 | bar | TBC | 150 | 4-20 mA Loop Powered | Subnet
22 | PIT-124951-002 | nQBMS | HW Supply Pressure Transmitter | Endress & Hauser | Cerabar PMP51B | G1/2 EN837 |  | n/a | PMP51B-AABACBA6AA3PBI1WBJA1+Z1 | n/a | n/a |  | 0 | 10 | Bar | TBC | 15 | 4-20 mA Loop Powered | Subnet
23 | PDT-124951-007 | nQBMS | HW Supply Pressure Differential Transmitter | Endress & Hauser | Deltabar PMD55B | G1/2 EN837 |  | n/a | PMD55B-AABACJA37HBGSAJA1B+F1JANRQ1Z1 | n/a | n/a |  | 0 | 6 | bar | TBC | 15 | 4-20 mA Loop Powered | Subnet
24 | PSH-124951-002 | nQBMS | HW Supply Pressure Switch High | Endress & Hauser | Cerabar PMP21 | G1/2 EN837 |  | RMA42 | PMP21-AA1A1NBWBJ+F3JAZ1 | n/a | n/a |  | 0 | 9.8 | bar | TBC | 15 | 4-20 mA Loop Powered | Subnet
25 | PDT-124951-002 | nQBMS | HW End of Line Pressure Differential Transmitter | Endress & Hauser | Deltabar PMD55B | G1/2 EN837 |  | n/a | PMD55B-AABACJA37HBGSAJA1B+F1JANRQ1Z1 | n/a | n/a |  | 0 | 6 | bar | TBC | 20 | 4-20 mA Loop Powered | Subnet
7 | TT-103212-501 | nQBMS | UF Water Flow Temperature Transmitter | Endress & Hauser | TM411 | Tri-Clamp | SS | n/a | TM411-6HDQ0/125 | 50 | 30 | UF | -10 | 100 | °C | TBC | 80 | 4-20 mA Loop Powered | Subnet
8 | TT-103212-502 | nQBMS | HHW Flow Temperature Transmitter | Endress & Hauser | TM121 | G1/2” Male Thread | SS | n/a | TM121-VEF6/101 | 60 | 40 | HHW | -10 | 100 | °C | TBC | 100 | 4-20 mA Loop Powered | Subnet
28 | FIT-124951-002 | nQBMS | HW Return Calorifier Flow Transmitter | Endress & Hauser | Proline Promag P300 | G1/2” male thread |  | n/a | TM121-HJXO/101 | n/a | n/a |  | 0 | 500 | l/min | 88 l/min | 50 | 4-20mA (Passive) | Subnet
29 | PDT-124951-006 | nQBMS | HW End of Line Pressure Differential Transmitter | Endress & Hauser | Deltabar PMD55B | G1/2 EN837 |  | n/a | PMD55B-AABACJA37HBGSAJA1B+F1JANRQ1Z1 | n/a | n/a |  | 0 | 6 | bar | TBC | 32 | 4-20 mA Loop Powered | Subnet
30 | PDT-124951-005 | nQBMS | HW End of Line Pressure Differential Transmitter | Endress & Hauser | Deltabar PMD55B | G1/2 EN837 |  | n/a | PMD55B-AABACJA37HBGSAJA1B+F1JANRQ1Z1 | n/a | n/a |  | 0 | 6 | bar | TBC | 20 | 4-20 mA Loop Powered | Subnet
31 | PDT-124951-003 |  | HW End of Line Pressure Differential Transmitter | Endress & Hauser | Deltabar PMD55B | G1/2 EN838 |  | n/a | PMD55B-AABACJA37HBGSAJA1B+F1JANRQ1Z1 | n/a | n/a |  | 0 | 6 | bar | TBC | 15 | 4-20 mA Loop Powered | Subnet
9 | TT-103212-503 | nQBMS | HHW Return Temperature Transmitter | Endress & Hauser | TM121 | G1/2” Male Thread | SS | n/a | TM121-VEF6/101 | 60 | 40 | HHW | -10 | 100 | °C | TBC | 100 | 4-20 mA Loop Powered | Subnet
10 | FIT-103212-500 | nQBMS | HHW Water Flow Meter | Endress & Hauser | Proline Promag W 10 | PN40 Flange EN-1092-1 | PTFE | n/a | 5WBB1H-RVR9/101 | n/a | n/a | HHW | 0 | 20 | l/s | TBC | 100 | 4-20 mA Loop Powered | Subnet
13 | FM-002B | nQBMS | UF Water Flow Meter | Endress & Hauser | Proline Promag P300 | PN40 Flange EN-1092-1 | PTFE | n/a | 5P3B80-264K0/101 | n/a | n/a | UF | 0 | 40 | l/s | TBC | 80 | 4-20 mA Loop Powered | Subnet | EM3 to confirm
35 | FIT-124600-001 | nQBMS | WFO to GMP Plantroom Flow Transmitter | Endress & Hauser | Proline Promag P300 | PN40 Flange EN-1092-1 |  | n/a | 5P3B25-AAIBAEAFAAED5K0AA2+AAZ1 | n/a | n/a |  | 0 | 300 | l/min | 48 l/min | 50 | 4-20mA (Passive) | Subnet |  | 25mm from Utilties package in our office
36 | FIT-124600-002 | nQBMS | Rainwater Storage Tank to Grey Water Flow Transmitter | Endress & Hauser | Proline Promag P300 | PN40 Flange EN-1092-1 |  | n/a | 5P3B15-AAIBAEAFAAED5K0AA2+AAZ1 | n/a | n/a |  | 0 | 100 | l/min | 30 l/min | 35 | 4-20mA (Passive) | Subnet
37 | PIT-124851-001 | nQBMS | Compressed Air Pressure Transmitter | Endress & Hauser | Cerabar PMP51B | G1/2 EN837 |  | n/a | PMP51B-AABACBA6AA3PBI1WBJA1+Z1 | n/a | n/a |  | 0 | 10 | Bar | 7 Bar | 80 | 4-20 mA Loop Powered | Subnet
38 | LT-124651-001 | nQBMS | GWS Break Tank Level Transmitter | Endress & Hauser | Micropilot FMR20 | TBC |  | TBC | FMR20-AAPBMWDEWFE2+R7Z1 | TBC | TBC |  | TBC | TBC | TBC | TBC | TBC | 4-20 mA Loop Powered | Subnet
39 | PIT-124151-001 | nQBMS | Condensate Supply Pressure Transmitter | Endress & Hauser | Cerabar PMP51B | G1/2 EN837 |  | n/a | PMP51B-AABACBA6AA3PBI1WBJA1+Z1 | n/a | n/a |  | 0 | 10 | Bar | 7 Bar | 15 | 4-20 mA Loop Powered | Subnet
14 | CV-001 | nQBMS | 2 Port Control Valve-Meco & BMS | Emerson | Fisher DX | TBC |  | TBC | TBC | TBC | TBC |  | TBC | TBC | TBC | TBC | TBC | TBC | TBC
41 | PIT-124151-002 |  | Condensate Supply Pressure Indication Transmitter | Endress & Hauser | Cerabar PMP51B | G1/2 EN837 |  | n/a | PMP51B-AABACBA6AA3PBI1WBJA1+Z1 | n/a | n/a |  | 0 | 10 | Bar | 7 Bar | 15 | 4-20 mA Loop Powered | Subnet

## RV Instrument SUB-TF-01
SECTION A - Project Details
Project |  |  |  | Client |  |  |  | Date (DD MMM YYYY)
Reference Document (Instrument Index) |  |  |  | Document Revision (1.0, 2.0 etc) |  |  |  | RV Form No.
SECTION B - Purchased Instrument Details
Instrument Tag |  | Make |  | Model Number |  | Order Code
Process connection / Mounting | Probe Immersion length |  | Signal Type |  | Instrument Range |  |  | Other
[5 empty] | Min | Max | Unit
SECTION C - Received Instrument Details
Instrument Tag |  | Make |  | Model Number |  | Order Code
Process connection / Mounting | Probe Immersion length |  | Signal Type |  | Instrument Range |  |  | Serial Number
[5 empty] | Min | Max | Unit
SECTION C - VERIFICATION / SIGN OFF
Company | Initials & Date |  | Result |  | Non-conformance no. N/A if not applicable |  |  | Date
☐ Pass ☐ Fail
☐ Pass ☐ Fail
SECTION D - COMMENTS N/A if not applicable